SHARED RESOURCE SERVICE

Summary of Internal Audit Activity

2024 – 25 Year to date

Introduction

The purpose of this report is to:

- Advise of the progress to date with the current year’s Audit Plan (2024 – 25)

- Provide details of the audits finalised in the period; and

- Raise any matters relevant to the Finance & Governance Board role.

Audit Plan 2024 - 25

Internal audit plan progress overview:

| STAGE; NUMBER; %AGE. NOT ISSUED (NID); 7; 63.64. ISSUED (ISS); 1; 9.09. FIELDWORK (FLD); 1; 9.09. REPORTING (REP); 0; 0.00. COMPLETED (COM); 2; 18.18. CODE; NARRATIVE. P; Planned. I; Issued. C; Completed. | Ref; Stage; Type; Title; Quarter. P; I; C. SRS - 24001; NID; FUP; Active Directory; 3. SRS – 24002; ISS; SYS; Application Integration Service; 2; 2. SRS – 24003; FLD; SYS; Business Management; 2; 2. SRS – 24004; COM; SYS; Data Centre – GPA; 1; 1; 2. SRS – 24005; NID; FUP; HALO; 3. SRS – 24006; COM; SYS; Information Security Management System; 1; 1; 2. SRS – 24007; NID; SYS; IT Disposals; 4. SRS – 24008; NID; SYS; IT Service Continuity Management; 4. SRS – 24009; NID; SYS; Mobile Computing; 2. SRS – 24010; NID; SYS; Software Asset Management; 3. SRS – 24011; NID; FUP; Solarwinds; 3. |
| --- | --- |

Audits Completed in the Period

| Audit Title: SRS – 24004 Data Centre - GPA |  | Audit Sponsor: Nigel Stephens / Matt Coe |  |  | Final Report Issued: 20 Aug 2024 |  |
| --- | --- | --- | --- | --- | --- | --- |
| Assurance Opinion: FULL; SUBSTANTIAL; MODERATE; LIMITED; NONE. | Recommendations / Management Action(s) |  |  |  |
| Audit Timeline: 96 days |  |  |  |  |  |  |
| ISS.1 |  |  |  |  |  | Priority: Medium |
| Control Requirement: Biometric or smart card access control devices are used to restrict access to the Data Centre, with all personnel entering from a designated entry point, with access monitored and the biometric/smart card activity logs reviewed/performed by an authorised person. There are procedures for disabling user access if biometric or smart card devices leave the organisation. Issue: The last 6-monthly review carried out by the FISO was on April 24th, 2024, using an access list prepared by the GWP Facilities team from the access card system. 10 of the 47 individuals were removed on April 25th, 2024, after confirming with estates/SRS that they no longer needed access or shouldn't have access, no other recommendations were made. The list contained an individual (PS) who had retired and left employment on 14th April as a leaver form had not been promptly completed. | Recommendation: Access control needs to be effectively managed; this requires robust monitoring and adherence to set procedure i.e. prompt completion, submission and processing of leaver forms. |  |  | Management Response: Agreed. Details of all SRS staff with data centre access will be sent to the Assistant Director, who will then from that point, notify the Head of Estates and the FISO to ensure that staff are promptly removed. Paul Higgs, Assistant Director August 31, 2024 |  |  |
| ISS.2 |  |  |  |  |  | Priority: Medium |
| Control Requirement: System downtime/outage is actively monitored to prevent service failure. Issue: The Data Centre at Vantage uses tools such as SCADA, PME and trend analysis. When questioned, management stated that the control was not in place even though it is known that a BMS exists. Whatever the arrangements in place they are not networked, and only on a local console in the room from which no performance data was provided as it had failed. In 2022 an engagement request for it to be networked was made but it is currently sitting on a horizons project list as it has not been prioritised by GPA. | Recommendation: The expected control(s) should be implemented, and management should receive the necessary assurance of its operation. Prioritisation of the engagement request would help provide the necessary assurance for management. |  |  | Management Response: Agreed. The BMS supplier is to visit to provide guidance which will result in a policy/procedure to be included in the data centre guide. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.3 |  |  |  |  |  | Priority: High |
| Control Requirement: A standard and approved data centre operating policy and guidance exists which guides the management and operation of the Data Centre and which all required persons are aware of. A mechanism for reviewing the operating manual on a regular basis to reflect changes and improvements in operations and verify adherence to best practice exists. Issue: Management stated that the controls were not in place. The existence of OEMs was mentioned, but these were not provided. | Recommendation: The expected control(s) should be implemented, and management should receive the necessary assurance of its operation. |  |  | Management Response: Agreed. An operating procedure (and guidance) will be devised and introduced. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.4 |  |  |  |  |  | Priority: Medium |
| Control Requirement: Controls are in place to adequately prevent floods and other disasters. Issue: A copy of the Business Continuity Plan was provided, it does not reference Disaster Recovery (DR) and no DR plan was provided. | Recommendation: A Disaster Recovery plan for the Data Centre should exist which is linked to/integrated with the Business Continuity Plan. |  |  | Management Response: Agreed. A disaster recovery plan will be produced for the Data Centre and included in the policy and procedures for HQ. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.5 |  |  |  |  |  | Priority: High |
| Control Requirement: Hardware automatically shuts down to protect itself from damage if unacceptable temperatures are reached. Issue: No evidence was provided to confirm that hardware automatically shuts down. | Recommendation: Management needs to ensure that it receives assurance on the measures that operate to protect items in the Data Centre. |  |  | Management Response: Agreed. The BMS supplier is to visit to provide guidance which will result in a policy/procedure to be included in the data centre guide. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.6 |  |  |  |  |  | Priority: Medium |
| Control Requirement: Utilisation rates are monitored to reduce the use of dedicated resources to a minimum. Issue: No information from the BMS was supplied. | Recommendation: Management needs to ensure that it receives assurance on the measures that operate to protect items in the Data Centre. |  |  | Management Response: Agreed. The BMS supplier is to visit to provide guidance which will result in a policy/procedure to be included in the data centre guide. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.7 |  |  |  |  |  | Priority: High |
| Control Requirement: The Data Centre has an appropriate redundancy level. Issue: Management stated that the control was not in place and no evidence of the level of redundancy in place if any, was provided. | Recommendation: Management needs to ensure that it receives assurance on the measures that operate to protect items in the Data Centre. |  |  | Management Response: Agreed. The data centre redundancy level will be documented in the operating procedure that will be produced. Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.8 |  |  |  |  |  | Priority: Medium |
| Control Requirement: Alerts and notifications have been set based on agreed resource thresholds so systems trigger/alert an operator when these are violated or exceeded. Issue: Management stated that alarms only operate on the FLAKT air conditioning units, with a call raised when a trigger is reached. It was noted that this is a manual process, and a significant time could elapse before identification. It was stated that no trigger/alert had been experienced in the last 3 years. | Recommendation: Management needs to ensure that an automated (rather than a manual) process is in place and operating. It should be sought to include FLAKT in the engagement request that is in place to provide networked monitoring. |  |  | Management Response: Agreed. Enquiries will be made with the supplier as to whether the alerts can be linked to the BMS. If possible then a procedure will be written and included in the operating policy. Any related costs will be included in the engagement request, which will be prioritised. Matt Coe, Chief Finance Officer Shaun Connolly, Head of Estates and Facilities Management November 30, 2024 |  |  |
| ISS.9 |  |  |  |  |  | Priority: Medium |
| Control Requirement: Performance measurement and monitoring systems have been implemented. Issue: Management stated that there was a Building Management System (not proactively reviewed) and the FLAKT. As no evidence was provided then no assurance can be given. | Recommendation: Management needs to seek assurance regarding the existence, adequacy and effectiveness of systems in place for performance measurement and monitoring. |  |  | Management Response: Agreed. Enquiries will be made with the supplier as to whether the alerts can be linked to the BMS. If possible then a procedure will be written and included in the operating policy. Any related costs will be included in the engagement request, which will be prioritised. Matt Coe, Chief Finance Officer November 30, 2024 |  |  |

| Audit Title: SRS – 24006 Information Security Management System | Audit Sponsor: Matt Lewis / Kathryn Beavan-Seymour |  | Final Report Issued: 06 Aug 2024 |
| --- | --- | --- | --- |
| Assurance Opinion: FULL; SUBSTANTIAL; MODERATE; LIMITED; NONE. | Recommendations / Management Action(s) |  |
| Audit Timeline: 111 days |  |  |  |

| ISS.1 – 5.29 Information Security During Disruption |  |  | Priority: Medium |
| --- | --- | --- | --- |
| Control Requirement: The Organisation shall: - determine its requirements for information security and the continuity of information security management in adverse situations, e.g. during a crisis or disaster. - establish, document, implement and maintain processes, procedures and controls to ensure the required level of continuity for information security during an adverse situation. - verify the established and implemented information security continuity controls at regular intervals to ensure that they are valid and effective during adverse situations. Issue: There is no list of established and implemented controls for Information Security during an adverse situation. Review of the Business Continuity Plan, and the linked playbooks failed to identify that: - the requirements for IS and its continuity in an adverse situation had been determined. - the processes, procedures and controls to ensure the required level of continuity for IS during an adverse situation had been documented. - IS continuity controls are verified at regular intervals to ensure they are valid and effective during adverse situations. | Recommendation: The objective of this control is that information security continuity shall be embedded in the organisation’s business continuity management systems. The organisation must determine its requirements for information security and the continuity of information security management in adverse situations. The organisation needs to establish, document, implement and maintain processes, procedures and controls to ensure the required level of continuity for information security during a disruptive situation. The organisation must verify the established and implemented information security continuity controls at regular intervals to ensure that they are valid and effective during these situations. The controls implemented for information security continuity must be tested, reviewed and evaluated periodically to ensure they are maintained against changes in the business, technologies and risk levels. . | Management Response: Agreed. We will review the information security playbooks in place, and the Business Continuity Plan to ensure that: - the requirements for IS and its continuity in an adverse situation have been determined. - the processes, procedures and controls to ensure the required level of continuity for IS during an adverse situation are documented. - IS continuity controls are verified at regular intervals to ensure they are valid and effective during an adverse situation. Helen Davies, Business Continuity Manager Rachel Titcombe, Information Security Architect December 31, 2024 |  |

Key Points to Note

Some audits have been rescheduled at the request of the SRS.

Audit Team

| Name | Position | Telephone | Email |
| --- | --- | --- | --- |
| Peter Williams | Head of Audit | 01495 742278 | Peter.williams@torfaen.gov.uk |
| Michael Corcoran | Group Auditor | 01495 742270 | Mike.corcoran@torfaen.gov.uk |
| Arran Rosser | Senior Auditor | 01495 742275 | Arran.rosser@torfaen.gov.uk |

Contact Information

Torfaen Internal Audit Service

Civic Centre, Pontypool NP4 6YB

Fax 01495 742439

mike.corcoran@torfaen.gov.uk